## Changes (hidden)
Changes
#01 original
#02 changes made from feedback received from JBB on 19/12/14
#03 changes made from feedback received from JBB on 16/1/15
#04 addition of 45oC, calculated based on the way SAP deals with 45oC if product performance information is not available, otherwise manufacturers test data
#05 MCS logo added, % difference removed from declared kW at 45
#06 Added graph of the SCOP figures to allow reading of mid points for MCS calculations
#07 SCOP calculated at flow temperatures between 35 and 55, factor changed to 0.5 for 45 conditions to give graph straight line as default.
#08 SCOP table added to ErP inputs tab
#09 Correction for 45oC data to include inputted data
Crankcase heater added
System SCOP changed to SCOP (equivalent to SPF3 SEPEMO SH only)
Rated heat output added to specify capacity of HP and supplementary for property load at -10oC
Bivalent temperature added to calculation tabs and ErP Inputs tab
#10 Selection menu changed on ErP Inputs to allow for Water Source heat pumps and GS & WS VHTHPs
SCOP amended to take account of the control and ground pump correction factors
#11 Bivalent temperature input removed from application temperature tabs
#12 Table reference corrected for ASHP's
#13 link to degradation coefficient for VHTHP corrected
#14 Energy Efficiency class changed to onl go up to A++
#15 Medium SCOP - Bivalent temperaure MIN value
#16 Condition E (TOL) - Bin temperature
#17 Low temperautre application class corrected
#18 Medium temperautre input reference corrected on 'Medium SCOP' tab, calculator now allows for TOL to -7oC,
#19 Bivalent temperature correction, uses N/A instead of 0, Interpolation at 45 Prated, TOL check added for ASHPs

## Scope
MCS 026 - SCOP and SSHEE calculator
This calculator can only be used for calculating the Seasonal Space Heating Energy Efficiency (SSHEE) and Seasonal Coefficient of Performance (SCOP) for Air to Water and Water / Brine to Water heat pumps under the average climate conditions defined by Commission Regulation (EU) No. 813/2013.
MCS Certification Bodies may use the calculator when certifying products against the requirements of MCS 007 - (Product certification scheme requirements - Heat pumps).
Data calculated in accordance with this calculator will be published within the product search section of the MCS database. Please visit http://www.microgenerationcertification.org/
The calculator is designed for use as an Microsoft Excel Macro-Enabled workbook.

## ErP Inputs
This calculator can only be used for calculating the Seasonal Space Heating Energy Efficiency (SSHEE) and Seasonal Coefficient of Performance (SCOP) for Air to Water and Water / Brine to Water heat pumps under the average climate conditions defined by Commission Regulation (EU) No. 813/2013
Grace Davies 27/08/11
Key
| 1 | Heat Generator? | Air Source | [9 empty] | Input Required
| 2 | Temperature Control? | Variable Outlet | [9 empty] | Calculated Outcomes
| 3 | Has the manufacturer provided data to demonstrate that the heat pump can reach a flow temperature of 52oC at Condition A according to the relevant product table within EN 14825 for the average climate and high temperature application? | Yes
| 4 | Has the manufacturer provided data to demonstrate that the heat pump can reach a flow temperature of 61oC or greater at an inlet dry (wet) bulb temperature of -7oC (-8oC) for ASHP OR Brine 0oC for Ground Source OR Water 10oC for Water Source Heat Pumps | Yes
|  | Classification under ErP | Heat Pump
|  | Classification under MCS | Very High Temperature Heat Pump
|  | Energy Label (Space Heater Only) to display SSHEE at | 55oC and 35oC
| Notes: | Low Temperature Heat Pumps only need to supply test data to 35oC | [12 empty] | Air Source
|  | Heat Pumps must supply test data at 35oC and 55oC | [12 empty] | Ground Source
|  | Very High Temperature Heat Pumps must supply test data to 35oC, 55oC and 65oC | [12 empty] | Water Source
[6 empty] | Flow Temperature (oC) | [8 empty] | Fixed Outlet
[6 empty] | 35 |  | 45 |  | 55 |  | 65 |  |  | Variable Outlet
|  | Rated Heat Output including the rated heat output of any supplementary heater under average climate conditions (kW) | [12 empty] | Yes
No
|  | All entries to 3 significant figures | Test Conditions EN 14825:2013 | A (88%) |  | B (54%) |  | C (35%) |  | D (15%) |  | E* (100%)
| Product Performance Data | Low Temperature Application (35oC) EN 14825:2013 - Table 12 (ASHP) or Table 24 (GSHP) |  | A-7 / W | 34 | A2 / W | 30 | A7 / W | 27 | A12 / W | 24 | A-10 / W | 35
|  |  | Heating Capacity (kW) | [10 empty] | Performance data always required |  | Average Climate
|  |  | Coefficient of Performance (kW/kW) | [10 empty] | Performance data always required |  | Variable Outlet Flow Temperatures
|  |  | Degradation coefficient Cc | [10 empty] | If the degradation coefficient is not specified, leave blank |  | -10 | -7 | 2 | 7 | 12
|  | High Temperature Application (55oC) EN 14825:2013 - Table 18 (ASHP) or Table 30 (GSHP) |  | A-7 / W | 52 | A2 / W | 42 | A7 / W | 36 | A12 / W | 30 | A-10 / W | 55 |  | Low | 35 | 34 | 30 | 27 | 24
|  |  | Heating Capacity (kW) | [10 empty] | Performance data required | Medium | 45 | 43 | 37 | 33 | 28
|  |  | Coefficient of Performance (kW/kW) | [10 empty] | Performance data required | High | 55 | 52 | 42 | 36 | 30
|  |  | Degradation coefficient Cc | [10 empty] | If the degradation coefficient is not specified, leave blank | Very High | 65 | 61 | 49 | 41 | 32
|  | Very High Temperature Application (65oC) EN 14825:2013 - Table 21 (ASHP) or Table 33 (GSHP) |  | A-7 / W | 61 | A2 / W | 49 | A7 / W | 41 | A12 / W | 32 | A-10 / W | 65
|  |  | Heating Capacity (kW) | [10 empty] | Performance data required
|  |  | Coefficient of Performance (kW/kW) | [10 empty] | Performance data required
|  |  | Degradation coefficient Cc | [10 empty] | If the degradation coefficient is not specified, leave blank
*If the declared Temperature Operation Limit (TOL) of the heat pump is lower than Tdesignh, then it may be assumed that TOL is equal to Tdesignh
Condition E - The design temperature (Tdesignh) for the average climate conditions is fixed at -10oC
Temperature application references are taken from EN 14825 NOT ErP definitions
|  | Temperature Operation Limit (TOL) | -22 | oC | Air to Water heat pumps must be capable of working at a temperature of -7oC or less
|  | Thermostat-off power (PTO) | 0.013 | kW
|  | Off power (POFF) | 0 | kW
|  | Crank Case Mode (PCK) | 0 | kW
The table below is only to be filled out if additional performance data is supplied by the manufacturer at the sink temperature of 45oC
| Product Performance Data | Medium Temperature Application (45oC) EN 14825:2013 - Table 18 (ASHP) or Table 30 (GSHP) |  | A-7 / W | 43 | A2 / W | 37 | A7 / W | 33 | A12 / W | 28 | A-10 / W | 45
|  |  | Heating Capacity (kW) | [10 empty] | This table is only to be completed in it entirety when performance data is supplied by the manufacturer at 45oC. Partial data is NOT to be accepted.
Coefficient of Performance (kW/kW)
Degradation coefficient Cc
OUTPUTS
| Application temperature | Seasonal Space Heating Energy Efficiency | Seasonal Coefficient of Performance | CLASS |  | Tbivalent oC
| Low (35°C) | #DIV/0! | #DIV/0! | #DIV/0! |  | N/A
| Medium (45°C) | #DIV/0! | #DIV/0! | #DIV/0! |  | N/A
| High (55°C) | #DIV/0! | #DIV/0! | #DIV/0! |  | N/A
| Very High (65°C) | #DIV/0! | #DIV/0! | #DIV/0! |  | N/A
#DIV/0!
Graph Data
[5 empty] | 35 | #DIV/0!
|  | System Design Flow Temperature | 35 |  | 45 | #DIV/0!
|  | System Seasonal Coefficient of Performance | #DIV/0! |  | 55 | #DIV/0!
[5 empty] | 65 | #DIV/0!
|  | Flow Temperature | SCOP (equivalent to SPF3 SEPEMO SH only) |  | 55 | #DIV/0!
|  | 35 | #DIV/0! |  | 65 | #DIV/0!
|  | 36 | #DIV/0!
|  | 37 | #DIV/0!
|  | 38 | #DIV/0!
|  | 39 | #DIV/0!
|  | 40 | #DIV/0!
|  | 41 | #DIV/0!
|  | 42 | #DIV/0!
|  | 43 | #DIV/0!
|  | 44 | #DIV/0!
|  | 45 | #DIV/0!
|  | 46 | #DIV/0!
|  | 47 | #DIV/0!
|  | 48 | #DIV/0!
|  | 49 | #DIV/0!
|  | 50 | #DIV/0!
|  | 51 | #DIV/0!
|  | 52 | #DIV/0!
|  | 53 | #DIV/0!
|  | 54 | #DIV/0!
|  | 55 | #DIV/0!
|  | 56 | #DIV/0!
|  | 57 | #DIV/0!
|  | 58 | #DIV/0!
|  | 59 | #DIV/0!
|  | 60 | #DIV/0!
|  | 61 | #DIV/0!
|  | 62 | #DIV/0!
|  | 63 | #DIV/0!
|  | 64 | #DIV/0!
|  | 65 | #DIV/0!
Cells highlighted red indicate at which flow temperature the Heat pump cannot achieve an SCOP of 2.5

## LOW SCOP
Summary
Climate | Average | [5 empty] | Table 1 Number of hours used for heating only - Average Climate |  |  |  |  | Thermostat-off power PTO | 0.013 | kW
Tdesignh | -10 | oC |  |  |  |  | On mode | Thermostat-off mode HTO | Standby mode HSB | Off mode HOFF | Crankcase heater mode HCK | Off power POFF | 0 | kW
Property Full load (Pdesignh) | 0 | kW |  |  |  | Average Climate (h/y) | 2066 | 178 | 0 | 3672 | 3850 | Crankcase heater power PCK | 0 | kW
[12 empty] | QH = Pdesignh x HHE | 0
[12 empty] | Annual Electrical consumption QHE | #DIV/0!
Air Source | [11 empty] | SCOP | #DIV/0!
Variable Outlet | [11 empty] | Conversion Coefficient | 2.5
[12 empty] | Correction Factor F(1) | 3 | %
Part Load Ratio |  |  | (Tj-16) / (-10-16) % | [8 empty] | Correction Factor F(2) | 0 | %
[12 empty] | Correction Factor F(i) | 3 | %
Condition | Bin Temperature | Outdoor heat exchanger | Indoor Heat exchanger | Part Load Ratio | Part Load | Declared Capacity | COP at Declared Capacity | Degradation coefficient | Capacity Ratio | Degradation Factor | COP at Part Load | Seasonal Space Heating Energy Efficiency | #DIV/0!
|  |  |  | % | kW | kW | COPDC | Cc | CR |  | COPPL
| -15 | Not Applicable | Not Applicable | [8 empty] | Seasonal Space Heating Energy Efficiency class | #DIV/0!
A | -7 | -7 | 34 | 88.46% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
B | 2 | 2 | 30 | 53.85% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | Bivalent Temperature | N/A | oC
C | 7 | 7 | 27 | 34.62% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! |  | TRUE
D | 12 | 12 | 24 | 15.38% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
E (TOL) | -10 | -10 | 35 | 100% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Bin | Outdoor temperature (dry bulb) | Hours | Part Load Ratio | Part Load | Annual Heating Demand | Heat Pump Capacity | Heat Load covered by HP | Electric back up heater | Annual Energy Input from Backup heater | COPPL | Annual Energy Input including electric backup heater | Net Annual heating capacity | Net Annual power input
j | Tj | hj |  | Ph(Tj) | hj x Ph(Tj) |  |  | elbu(Tj) | hj x elbu(Tj) |  | hj x [Ph(Tj) - elbu(Tj) / COPPL(Tj) + elbu(Tj)] | hj x {Ph(Tj) - elbu(Tj)} | hj x Ph(Tj) - elbu(Tj) / COPPL(Tj)
| oC | h |  | kW | kWh | kW | kW | kW | kWh |  | kWh | kWh | kWh
21 | -10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -10 | -10
22 | -9 | 25 | 0.96154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -9 | -9
23 | -8 | 23 | 0.92308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -8 | -8
24 | -7 | 24 | 0.88462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -7 | -7
25 | -6 | 27 | 0.84615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -6 | -6
26 | -5 | 68 | 0.80769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -5 | -5
27 | -4 | 91 | 0.76923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -4 | -4
28 | -3 | 89 | 0.73077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -3 | -3
29 | -2 | 165 | 0.69231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -2 | -2
30 | -1 | 173 | 0.65385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -1 | -1
31 | 0 | 240 | 0.61538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0
32 | 1 | 280 | 0.57692 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 1 | 1
33 | 2 | 320 | 0.53846 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 2 | 2
34 | 3 | 357 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 3 | 3
35 | 4 | 356 | 0.46154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 4 | 4
36 | 5 | 303 | 0.42308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 5 | 5
37 | 6 | 330 | 0.38462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 6 | 6
38 | 7 | 326 | 0.34615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 7 | 7
39 | 8 | 348 | 0.30769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 8 | 8
40 | 9 | 335 | 0.26923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 9 | 9
41 | 10 | 315 | 0.23077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 10 | 10
42 | 11 | 215 | 0.19231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 11 | 11
43 | 12 | 169 | 0.15385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 12 | 12
44 | 13 | 151 | 0.11538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 13 | 13
45 | 14 | 105 | 0.076923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 14 | 14
46 | 15 | 74 | 0.038462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 15 | 15
|  | 4910 |  |  | 0 |  |  |  | 0 |  | #DIV/0! | 0 | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Note on J5: Commission Communication 2014/C 207/02
Note on K17: Default degradation coefficient equals 0.9
Note on L17: When the declared capacity is lower than the part load, the value of CR is considered to be 1 and thus COPbin(Tj) equal to COPd.

## MEDIUM SCOP
Summary
Climate | Average | [5 empty] | Table 1 Number of hours used for heating only - Average Climate |  |  |  |  | Thermostat-off power PTO | 0.013 | kW
Tdesignh | -10 | oC |  |  |  |  | On mode | Thermostat-off mode HTO | Standby mode HSB | Off mode HOFF | Crankcase heater mode HCK | Off power POFF | 0 | kW
Property Full load (Pdesignh) | 0 | kW |  |  |  | Average Climate (h/y) | 2066 | 178 | 0 | 3672 | 3850 | Crankcase heater power PCK | 0 | kW
[12 empty] | QH = Pdesignh x HHE | 0
[12 empty] | Annual Electrical consumption QHE | #DIV/0!
Air Source | [11 empty] | SCOP | #DIV/0!
Variable Outlet | [11 empty] | Conversion Coefficient | 2.5
[12 empty] | Correction Factor F(1) | 3 | %
Part Load Ratio |  |  | (Tj-16) / (-10-16) % | [8 empty] | Correction Factor F(2) | 0 | %
[12 empty] | Correction Factor F(i) | 3 | %
Condition | Bin Temperature | Outdoor heat exchanger | Indoor Heat exchanger | Part Load Ratio | Part Load | Declared Capacity | COP at Declared Capacity | Degradation coefficient | Capacity Ratio | Degradation Factor | COP at Part Load | Seasonal Space Heating Energy Efficiency | #DIV/0!
|  |  |  | % | kW | kW | COPDC | Cc | CR |  | COPPL
| -15 | Not Applicable | Not Applicable | [8 empty] | Seasonal Space Heating Energy Efficiency class | #DIV/0!
A | -7 | -7 | 43 | 88.46% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
B | 2 | 2 | 37 | 53.85% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | Bivalent Temperature | N/A | oC
C | 7 | 7 | 33 | 34.62% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! |  | TRUE
D | 12 | 12 | 28 | 15.38% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
E (TOL) | -10 | -10 | 45 | 100% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Bin | Outdoor temperature (dry bulb) | Hours | Part Load Ratio | Part Load | Annual Heating Demand | Heat Pump Capacity | Heat Load covered by HP | Electric back up heater | Annual Energy Input from Backup heater | COPPL | Annual Energy Input including electric backup heater | Net Annual heating capacity | Net Annual power input
j | Tj | hj |  | Ph(Tj) | hj x Ph(Tj) |  |  | elbu(Tj) | hj x elbu(Tj) |  | hj x [Ph(Tj) - elbu(Tj) / COPPL(Tj) + elbu(Tj)] | hj x {Ph(Tj) - elbu(Tj)} | hj x Ph(Tj) - elbu(Tj) / COPPL(Tj)
| oC | h |  | kW | kWh | kW | kW | kW | kWh |  | kWh | kWh | kWh
21 | -10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -10 | -10
22 | -9 | 25 | 0.96154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -9 | -9
23 | -8 | 23 | 0.92308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -8 | -8
24 | -7 | 24 | 0.88462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -7 | -7
25 | -6 | 27 | 0.84615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -6 | -6
26 | -5 | 68 | 0.80769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -5 | -5
27 | -4 | 91 | 0.76923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -4 | -4
28 | -3 | 89 | 0.73077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -3 | -3
29 | -2 | 165 | 0.69231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -2 | -2
30 | -1 | 173 | 0.65385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -1 | -1
31 | 0 | 240 | 0.61538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0
32 | 1 | 280 | 0.57692 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 1 | 1
33 | 2 | 320 | 0.53846 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 2 | 2
34 | 3 | 357 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 3 | 3
35 | 4 | 356 | 0.46154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 4 | 4
36 | 5 | 303 | 0.42308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 5 | 5
37 | 6 | 330 | 0.38462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 6 | 6
38 | 7 | 326 | 0.34615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 7 | 7
39 | 8 | 348 | 0.30769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 8 | 8
40 | 9 | 335 | 0.26923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 9 | 9
41 | 10 | 315 | 0.23077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 10 | 10
42 | 11 | 215 | 0.19231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 11 | 11
43 | 12 | 169 | 0.15385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 12 | 12
44 | 13 | 151 | 0.11538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 13 | 13
45 | 14 | 105 | 0.076923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 14 | 14
46 | 15 | 74 | 0.038462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 15 | 15
|  | 4910 |  |  | 0 |  |  |  | 0 |  | #DIV/0! | 0 | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Note on J5: Commission Communication 2014/C 207/02
Note on K17: Default degradation coefficient equals 0.9
Note on L17: When the declared capacity is lower than the part load, the value of CR is considered to be 1 and thus COPbin(Tj) equal to COPd.

## HIGH SCOP
Summary
Climate | Average | [5 empty] | Table 1 Number of hours used for heating only - Average Climate |  |  |  |  | Thermostat-off power PTO | 0.013 | kW
Tdesignh | -10 | oC |  |  |  |  | On mode | Thermostat-off mode HTO | Standby mode HSB | Off mode HOFF | Crankcase heater mode HCK | Off power POFF | 0 | kW
Property Full load (Pdesignh) | 0 | kW |  |  |  | Average Climate (h/y) | 2066 | 178 | 0 | 3672 | 3850 | Crankcase heater power PCK | 0 | kW
[12 empty] | QH = Pdesignh x HHE | 0
[12 empty] | Annual Electrical consumption QHE | #DIV/0!
Air Source | [11 empty] | SCOP | #DIV/0!
Variable Outlet | [11 empty] | Conversion Coefficient | 2.5
[12 empty] | Correction Factor F(1) | 3 | %
Part Load Ratio |  |  | (Tj-16) / (-10-16) % | [8 empty] | Correction Factor F(2) | 0 | %
[12 empty] | Correction Factor F(i) | 3 | %
Condition | Bin Temperature | Outdoor heat exchanger | Indoor Heat exchanger | Part Load Ratio | Part Load | Declared Capacity | COP at Declared Capacity | Degradation coefficient | Capacity Ratio | Degradation Factor | COP at Part Load | Seasonal Space Heating Energy Efficiency | #DIV/0!
|  |  |  | % | kW | kW | COPDC | Cc | CR |  | COPPL
| -15 | Not Applicable | Not Applicable | [8 empty] | Seasonal Space Heating Energy Efficiency class | #DIV/0!
A | -7 | -7 | 52 | 88.46% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
B | 2 | 2 | 42 | 53.85% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | Bivalent Temperature | N/A | oC
C | 7 | 7 | 36 | 34.62% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! |  | TRUE
D | 12 | 12 | 30 | 15.38% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
E (TOL) | -10 | -10 | 55 | 100% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Bin | Outdoor temperature (dry bulb) | Hours | Part Load Ratio | Part Load | Annual Heating Demand | Heat Pump Capacity | Heat Load covered by HP | Electric back up heater | Annual Energy Input from Backup heater | COPPL | Annual Energy Input including electric backup heater | Net Annual heating capacity | Net Annual power input
j | Tj | hj |  | Ph(Tj) | hj x Ph(Tj) |  |  | elbu(Tj) | hj x elbu(Tj) |  | hj x [Ph(Tj) - elbu(Tj) / COPPL(Tj) + elbu(Tj)] | hj x {Ph(Tj) - elbu(Tj)} | hj x Ph(Tj) - elbu(Tj) / COPPL(Tj)
| oC | h |  | kW | kWh | kW | kW | kW | kWh |  | kWh | kWh | kWh
21 | -10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -10 | -10
22 | -9 | 25 | 0.96154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -9 | -9
23 | -8 | 23 | 0.92308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -8 | -8
24 | -7 | 24 | 0.88462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -7 | -7
25 | -6 | 27 | 0.84615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -6 | -6
26 | -5 | 68 | 0.80769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -5 | -5
27 | -4 | 91 | 0.76923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -4 | -4
28 | -3 | 89 | 0.73077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -3 | -3
29 | -2 | 165 | 0.69231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -2 | -2
30 | -1 | 173 | 0.65385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -1 | -1
31 | 0 | 240 | 0.61538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0
32 | 1 | 280 | 0.57692 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 1 | 1
33 | 2 | 320 | 0.53846 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 2 | 2
34 | 3 | 357 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 3 | 3
35 | 4 | 356 | 0.46154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 4 | 4
36 | 5 | 303 | 0.42308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 5 | 5
37 | 6 | 330 | 0.38462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 6 | 6
38 | 7 | 326 | 0.34615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 7 | 7
39 | 8 | 348 | 0.30769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 8 | 8
40 | 9 | 335 | 0.26923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 9 | 9
41 | 10 | 315 | 0.23077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 10 | 10
42 | 11 | 215 | 0.19231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 11 | 11
43 | 12 | 169 | 0.15385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 12 | 12
44 | 13 | 151 | 0.11538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 13 | 13
45 | 14 | 105 | 0.076923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 14 | 14
46 | 15 | 74 | 0.038462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 15 | 15
|  | 4910 |  |  | 0 |  |  |  | 0 |  | #DIV/0! | 0 | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Note on J5: Commission Communication 2014/C 207/02
Note on K17: Default degradation coefficient equals 0.9
Note on L17: When the declared capacity is lower than the part load, the value of CR is considered to be 1 and thus COPbin(Tj) equal to COPd.

## VERY HIGH SCOP
Summary
Climate | Average | [5 empty] | Table 1 Number of hours used for heating only - Average Climate |  |  |  |  | Thermostat-off power PTO | 0.013 | kW
Tdesignh | -10 | oC |  |  |  |  | On mode | Thermostat-off mode HTO | Standby mode HSB | Off mode HOFF | Crankcase heater mode HCK | Off power POFF | 0 | kW
Property Full load (Pdesignh) | 0 | kW |  |  |  | Average Climate (h/y) | 2066 | 178 | 0 | 3672 | 3850 | Crankcase heater power PCK | 0 | kW
[12 empty] | QH = Pdesignh x HHE | 0
[12 empty] | Annual Electrical consumption QHE | #DIV/0!
Air Source | [11 empty] | SCOP | #DIV/0!
Variable Outlet | [11 empty] | Conversion Coefficient | 2.5
[12 empty] | Correction Factor F(1) | 3 | %
Part Load Ratio |  |  | (Tj-16) / (-10-16) % | [8 empty] | Correction Factor F(2) | 0 | %
[12 empty] | Correction Factor F(i) | 3 | %
Condition | Bin Temperature | Outdoor heat exchanger | Indoor Heat exchanger | Part Load Ratio | Part Load | Declared Capacity | COP at Declared Capacity | Degradation coefficient | Capacity Ratio | Degradation Factor | COP at Part Load | Seasonal Space Heating Energy Efficiency | #DIV/0!
|  |  |  | % | kW | kW | COPDC | Cc | CR |  | COPPL
| -15 | Not Applicable | Not Applicable | [8 empty] | Seasonal Space Heating Energy Efficiency class | #DIV/0!
A | -7 | -7 | 61 | 88.46% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
B | 2 | 2 | 49 | 53.85% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | Bivalent Temperature | N/A | oC
C | 7 | 7 | 41 | 34.62% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! |  | TRUE
D | 12 | 12 | 32 | 15.38% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
E (TOL) | -10 | -10 | 65 | 100% | 0 | 0 | 0 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Bin | Outdoor temperature (dry bulb) | Hours | Part Load Ratio | Part Load | Annual Heating Demand | Heat Pump Capacity | Heat Load covered by HP | Electric back up heater | Annual Energy Input from Backup heater | COPPL | Annual Energy Input including electric backup heater | Net Annual heating capacity | Net Annual power input
j | Tj | hj |  | Ph(Tj) | hj x Ph(Tj) |  |  | elbu(Tj) | hj x elbu(Tj) |  | hj x [Ph(Tj) - elbu(Tj) / COPPL(Tj) + elbu(Tj)] | hj x {Ph(Tj) - elbu(Tj)} | hj x Ph(Tj) - elbu(Tj) / COPPL(Tj)
| oC | h |  | kW | kWh | kW | kW | kW | kWh |  | kWh | kWh | kWh
21 | -10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -10 | -10
22 | -9 | 25 | 0.96154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -9 | -9
23 | -8 | 23 | 0.92308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | -8 | -8
24 | -7 | 24 | 0.88462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -7 | -7
25 | -6 | 27 | 0.84615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -6 | -6
26 | -5 | 68 | 0.80769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -5 | -5
27 | -4 | 91 | 0.76923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -4 | -4
28 | -3 | 89 | 0.73077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -3 | -3
29 | -2 | 165 | 0.69231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -2 | -2
30 | -1 | 173 | 0.65385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | -1 | -1
31 | 0 | 240 | 0.61538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0
32 | 1 | 280 | 0.57692 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 1 | 1
33 | 2 | 320 | 0.53846 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 2 | 2
34 | 3 | 357 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 3 | 3
35 | 4 | 356 | 0.46154 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 4 | 4
36 | 5 | 303 | 0.42308 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 5 | 5
37 | 6 | 330 | 0.38462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 6 | 6
38 | 7 | 326 | 0.34615 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 7 | 7
39 | 8 | 348 | 0.30769 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 8 | 8
40 | 9 | 335 | 0.26923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 9 | 9
41 | 10 | 315 | 0.23077 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 10 | 10
42 | 11 | 215 | 0.19231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 11 | 11
43 | 12 | 169 | 0.15385 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 12 | 12
44 | 13 | 151 | 0.11538 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 13 | 13
45 | 14 | 105 | 0.076923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 14 | 14
46 | 15 | 74 | 0.038462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 15 | 15
|  | 4910 |  |  | 0 |  |  |  | 0 |  | #DIV/0! | 0 | #DIV/0!
[10 empty] | SCOPON | #DIV/0! | SCOPNET | #DIV/0!
Note on J5: Commission Communication 2014/C 207/02
Note on K17: Default degradation coefficient equals 0.9
Note on L17: When the declared capacity is lower than the part load, the value of CR is considered to be 1 and thus COPbin(Tj) equal to COPd.

## Table 37
Table 37 - j,Tj& hj reference heating seasons
|  | Warmer | Average | Colder
j | Tj | hjW | hjA | hjC
| °C | h | h | h
1 | -30 | 0 | 0 | 0
2 | -29 | 0 | 0 | 0
3 | -28 | 0 | 0 | 0
4 | -27 | 0 | 0 | 0
5 | -26 | 0 | 0 | 0
6 | -25 | 0 | 0 | 0
7 | -24 | 0 | 0 | 0
8 | -23 | 0 | 0 | 0
9 | -22 | 0 | 0 | 1
10 | -21 | 0 | 0 | 6
11 | -20 | 0 | 0 | 13
12 | -19 | 0 | 0 | 17
13 | -18 | 0 | 0 | 19
14 | -17 | 0 | 0 | 26
15 | -16 | 0 | 0 | 39
16 | -15 | 0 | 0 | 41
17 | -14 | 0 | 0 | 35
18 | -13 | 0 | 0 | 52
19 | -12 | 0 | 0 | 37
20 | -11 | 0 | 0 | 41
21 | -10 | 0 | 1 | 43
22 | -9 | 0 | 25 | 54
23 | -8 | 0 | 23 | 90
24 | -7 | 0 | 24 | 125
25 | -6 | 0 | 27 | 169
26 | -5 | 0 | 68 | 195
27 | -4 | 0 | 91 | 278
28 | -3 | 0 | 89 | 306
29 | -2 | 0 | 165 | 454
30 | -1 | 0 | 173 | 385
31 | 0 | 0 | 240 | 490
32 | 1 | 0 | 280 | 533
33 | 2 | 3 | 320 | 380
34 | 3 | 22 | 357 | 228
35 | 4 | 63 | 356 | 261
36 | 5 | 63 | 303 | 279
37 | 6 | 175 | 330 | 229
38 | 7 | 162 | 326 | 269
39 | 8 | 259 | 348 | 233
40 | 9 | 360 | 335 | 230
41 | 10 | 428 | 315 | 243
42 | 11 | 430 | 215 | 191
43 | 12 | 503 | 169 | 146
44 | 13 | 444 | 151 | 150
45 | 14 | 384 | 105 | 97
46 | 15 | 294 | 74 | 61
| Total | 3590 | 4910 | 6446

## Version Control
AMENDMENTS SINCE PUBLICATION
Date | Issue | Notes
2015-05-01 | 1 | First version published